## Sample Data
|  | AHU Data | [21 empty] | Unit Weight [lbs] | Notes
|  | Manufacturer | Model Number | CAV/VAV | Airflow Data [CFM] |  |  | Supply Fan Data |  |  |  | Return Fan Data |  |  |  | Heating Data |  |  |  | Cooling Data
[5 empty] | Total Supply Air | Outside Air | Return Air | HP | Voltage | Phase | Hz | HP | Voltage | Phase | Hz | MBH | EAT [deg F] | RAT [deg F] | SAT [deg F] | MBH | EAT [deg F] | RAT [deg F] | SAT [deg F]
| Design | Trane | ABC-123-SW | VAV | 12000 | 7000 | 5000 | 5 | 208 | 3 | 60 | 3 | 208 | 3 | 60 | 120 | 0 | 75 | 60 | 220 | 95 | 75 | 65 | 2200 | Integrated VFD
| Alt. 1 | Greenheck | XYZ-789-RF | VAV | 12500 | 7500 | 5000 | 5 | 208 | 3 | 60 | 3 | 208 | 3 | 60 | 115 | 0 | 75 | 60 | 225 | 95 | 75 | 65 | 1900 | No VFD
| Alt. 2 | York | GHI-567-SK | CAV | 10500 | 10500 | 0 | 5 | 110 | 1 | 60 | N/A | N/A | N/A | N/A | 80 | 0 | N/A | 50 | 160 | 85 | 75 | 70 | 2600 | N/A
Color Key |  |  | Operation Notes
Same |  |  | 1. If the manufacture & model number is different, that is not a gamechanger - I chose pale red for this to highlight a difference, but a 'no-impact one'.
Better |  |  | 2. If the alternative data is better than the design data, I have highlighted this in green. This is a difference that is acceptable.
Worse |  |  | 3. If the alternative data is worse than the design data, I have highlighted this in red.
Different - No impact |  |  | 4. See Better-Worse Tab to discern how to tell what is better or worse. The Designer will input this criteria when uploading.
5. If a product from an alternative manufacturer is 'approved' a note should be included in the 'approval' that the Contractor becomes responsible for any coordination discrepancies.
6. If the Contractor is aware that one criteria will be worse than the design intent, an 'Additional Information' text box should be included to allow the Contractor to justify this.
6.a. This means that, when the product is forwarded to the Designer for review, the Designer can evaluate the whole system. For example, under Alt 2, there is no VFD provided [Notes]. The Contractor might be opting for a non-integrated product, which is compatible with the motors.

## Better-Worse
Manufacturer |  | Can vary
Model Number |  | Can vary
CAV/VAV |  | Must be the same as design
Airflow Data [CFM] | Total Air Supply | More is better | Less is worse
| Outside Air | More is better | Less is worse
| Return Air | More is better | Less is worse
Supply Fan Data | HP | Must be the same as design
| Voltage | Must be the same as design
| Phase | Must be the same as design
| Hz | Must be the same as design
Return Fan Data | HP | Must be the same as design
| Voltage | Must be the same as design
| Phase | Must be the same as design
| Hz | Must be the same as design
Heating Data | MBH | More is better | Less is worse
| EAT | Less is better | More is worse
| RAT | Less is better | More is worse
| SAT | More is better | Less is worse
Cooling Data | MBH | More is better | Less is worse
| EAT | More is better | Less is worse
| RAT | More is better | Less is worse
| SAT | Less is better | More is worse
Unit Weight |  | Less is better | More is worse
Notes |  | Must be the same as design